## Cover Page
2016 Risk Assessment Mitigation Phase
Investigation 16-10-015
Risk Spend Efficiency Workpapers to
Fail to Blackstart
(Chapter SDG&E-6-WP-RSE)
January 2017

## Analysis
Risk | SDGE - Fail to Black Start | [11 empty] | Likelihood of Failure to Blackstart Before Mitigations (given SDGE in blackout) = 0.0183
Less than 8 hours: 20.5% of the time
Baseline Residual Risk | [12 empty] | Probability = SDGE in blackout (given) * neighbors in blackout * Palomar unavailable * 20.5%
Adjustment Factor | Score Category | Scores | Original Baseline
0.018257 | Frequency | 0.018257 | 44548.1013 | [9 empty] | Greater than 8 hours: 79.5% of the time
| Safety Consequence | 6 | [10 empty] | Probability = SDGE in blackout (given) * neighbors in blackout * (Palomar unavailable or Palomar available but batteries fail) * 79.5%
| Reliability Consequence | 7
| Compliance Consequence | 5 | [10 empty] | Total = SDGE in blackout (given) * neighbors in blackout * Palomar unavailable * 20.5% + SDGE in blackout (given) * neighbors in blackout * (Palomar unavailable or Palomar available but batteries fail) * 79.5%
| Financial Consequence | 5
The adjustment factor was used to account for this risk to be contingent on having a blackout.
[14 empty] | Baseline |  | 6 | 7 | 5 | 5
[8 empty] | (000s) | [6 empty] | ↓Probability of a failure to blackstart | 40% | 20% | 20% | 20% | New Consequence Scores, weighted | [10 empty] | Ordered Mitigations | Ordered Cumulative New Score | Ordered Cumulative Cost | RSE
| Controls | Enable |  |  | Project ID | Name | Description | Capital Cost (2017-2019) | OM Cost (2017-2019 average) | Annuity | New/Existing | Life of the Project | Rationale | Frequency % | New Frequency | Safety | Reliability | Compliance | Financial | Safety | Reliability | Compliance | Financial | New Score | New Score (for life of project) | Mitigation Weight | Adjusted, Weighted New Score | Cost | RSE | Rank |  | 0 | 0
| Adjusted Baseline | 0 |  | 2016-10-19 | B1 & B2 | Maintenance, Certification, and testing of existing Blackstart Resources & Blackstart training and procedure development | • MEF I and II blackstart generators maintenance and testing programs • Biannual certification of MEF I and II as blackstart units • Maintenance of Orange Grove as a blackstart ressource through current Power Purchase Agreement (PPA)(SDG&E does not incur any cost specific to this mitigation) • Annual SDG&E blackstart/system restoration training and drill • Development and coordination of Blackstart plans with CAISO, Peak RC, and neighboring utilities through annual SDG&E EOP5005 procedure update | 0 | -79.598 | 0 | Existing | 1 | Over time, the likelihood of failure to blackstart, without maintenance and training, will increase to 100%. After 3 years, the likelihood of failure will go to 30%. (The likelihood of being able to blackstart, after 1 year of no training or maintenace, was assumed to be around 80-90%; after 2 years, 70-80%; after 3 years, 40-60%. This is an average of 70% success over the 3 years. The average likelihood of failing to blackstart, after 3 years, was therefore assumed to be 30%.) | -1543.1677 | 0.3 | 0 | 0 | 0 | 0 | 400000 | 2000000 | 20000 | 20000 | 732000 | -687451.8987 |  | -12551.0971 | -79.598 | 157.6811 | 1 | B1 & B2 | 12551.0971 | 79.598 | 157.6811 | B1 & B2 | Maintenance, certification, testing, and training
| Weights on Each Mitigation | 0 |  | 2016-10-19 | P1 | The South Grid Black-Start Project | Add blackstart capabilities to the southern part of the SDG&E electric system | 1235 | 0 | 125.7875 | New | 20 | This mitigation provides a redundancy to Palomar. New Probability = neighbors in blackout * [20.5% * Palomar unavailable * Redundant Path Unavailable + 79.5% * ((Palomar unavailable * Redundant Path unavailale or Redundant Path available but batteries fail) + Palomar available but batteries fail * Redundant Path unavailale or Redundant Path available but batteries fail)] | 65.9209 | 0.006222 | 0 | 0 | 0 | 0 | 400000 | 2000000 | 20000 | 20000 | 15181.5712 | 587330.6037 |  | 10723.1407 | 1235 | 8.6827 | 2 | P1 | 23274.2377 | 1314.598 | 8.6827 | P1 | The South Grid Black-Start Project
| Annuity instead of Capital Cost | 0 |  | 2016-10-19 | P2 | Transmission Energy Management System Modernization Project | Upgrade antiquated EMS visualization tool and control room. | 14629 | 0 | 1299.4565 | New | 30 | The new visualization tool reduces the likelihood of failing to blackstart by 10%. New probability = original probability of failure to blackstart * 90% | 10 | 0.016432 | 0 | 0 | 0 | 0 | 400000 | 2000000 | 20000 | 20000 | 40093.2866 | 133644.4434 |  | 2440.0025 | 14629 | 0.16679 | 4 | P3 | 24892.7617 | 6272.598 | 0.32645 | P3 | Substation Auxillary Power System (fuel cells)
| Adjustment Factor | 1 |  | 2016-10-19 | P3 | Substation Auxillary Power System (fuel cells) | Use fuel cells to provide backup power at major substations and substations on the Blackstart Cranking Paths. | 4958 | 0 | 738.8882 | New | 10 | With this mitigation, events lasting longer than 8 hours can still be blackstarted 100% of the time, if Palomar is available. New Probability = neighbors in blackout * 100% * Palomar unavailable | 19.8999 | 0.014624 | 0 | 0 | 0 | 0 | 400000 | 2000000 | 20000 | 20000 | 35683.0808 | 88650.2055 |  | 1618.5239 | 4958 | 0.32645 | 3 | P2 | 27332.7642 | 20901.598 | 0.16679 | P2 | Transmission Energy Management System Modernization Project
Probability
| 7 | 31.6228
| 6 | 3.1623
| 5 | 0.57735
| 4 | 0.18257
| 3 | 0.057735
| 2 | 0.018257
| 1 | 0.0057735
Annual or total?

## Summary
Project ID | Name |  | Capital Cost (Life of Project) | OM Cost (Annual) | Life of the Project | Derived New Scores | Cost | RSE | Rank
B1 | Maintenance, Certification, and testing of existing Blackstart Ressources | • MEF I and II blackstart generators maintenance and testing programs • Biannual certification of MEF I and II as blackstart units • Maintenance of Orange Grove as a blackstart ressource through current Power Purchase Agreement (PPA)(SDG&E does not incur any cost specific to this mitigation) | 0 | 39.799 | 1 | 6275.5485 | 39.799 | 157.6811 | 1
B2 | Blackstart training and procedure development | • Annual SDG&E blackstart/system restoration training and drill • Development and coordination of Blackstart plans with CAISO, Peak RC, and neighboring utilities through annual SDG&E EOP5005 procedure update | 0 | 39.799 | 1 | 6275.5485 | 39.799 | 157.6811 | 1
P1 | The South Grid Black-Start Project | Add blackstart capabilities to the southern part of the SDG&E electric system | 1235 | 0 | 20 | 10723.1407 | 1235 | 8.6827 | 3
P2 | Transmission Energy Management System Modernization Project | Upgrade antiquated EMS visualization tool and control room. | 14629 | 0 | 10 | 2440.0025 | 14629 | 0.16679 | 5
P3 | Substation Auxillary Power System (fuel cells) | Use fuel cells to provide backup power at major substations and substations on the Blackstart Cranking Paths. | 4958 | 0 | 10 | 1618.5239 | 4958 | 0.32645 | 4

## Likelihood Before
Before
Blackout less than 8 hours: |  |  | 0.002998
20.5% of the time
| 0.91225 | At least one neighbor on interconnect is not blacked out
Successful Blackstart
[7 empty] | 1 | At least 1 craking path available
Successful Blackstart
SDG&E is in blackout (given) |  |  |  | 0.83333 | Palomar is not undergoing maintenance
Cranking paths are in parallel, rather than in sequence.
[7 empty] | 1.411e-07 | Both cranking paths unavailable |  | Path 1 unavailable 89.92 minutes per year, or 0.00017
[9 empty] | failure to blackstart | Path 2 unavailable 462.65 minutes per year, or 0.00083
| 0.087745 | All 4 critical neighboring interconnect utilities affected
|  |  |  | 0.16667 | Palomar is unavailable (2 months/year)
failure to blackstart
Blackout greater than 8 hours: |  |  | 0.015259
79.5% of the time
| 0.91225 | At least one neighbor on interconnect is not blacked out |  |  |  |  | 0.9375 | Batteries work for both cranking paths
Successful Blackstart
SDG&E is in blackout (given) |  |  |  | 83.33% | Palomar is available
| 0.087745 | All 4 critical neighboring interconnect utilities affected |  |  |  |  | 0.0625 | Batteries fail for both cranking paths
failure to blackstart
|  |  |  | 16.67% | Palomar is unavailable (batteries expired after 8 hours)
failure to blackstart
Failure to Blackstart Likelihood (given SDG&E is in a blackout)
0.018257 |  |  | P=Failure to blackstart; PN=neighbors out; PPU=Palomar unavailable; PBF=batteries fail
This was given a score of 2 |  |  | P=PN*[0.205*(PPU)+0.795*(PPU+(1-PPU)*PBF)]
0.0183=PN*[0.205*(1/6)+0.795*(1/6+5/6*0.25*0.25)]
PN=0.088
This is basically 0

## P1
P1
Redundant Path
P=PN*[0.205*(PPU)*[Redundant Path Unavailable]+0.795*(PPU*[Redundant Path Unavailable or available but batteries fail]+(1-PPU)*PBF*[Redundant Path Unavailable or available but batteries fail])]
Less than 8 hours = likelihood before * Probability of new path unavailable
Probability of New Path Unavailable
16.67% | *SME (8/18): For the availability of Pio Pico, it might be better to use the availability of Palomar (1/6 unavailable) |  | 0.00049966
Greater than 8 hours = (see below) |  |  | 0.0057223
New P1 Likelihood |  |  | 0.006222
Blackout less than 8 hours: |  |  |  | 0.00049966
20.5% of the time
|  | 0.91225 | At least one neighbor on interconnect is not blacked out
Successful Blackstart
[6 empty] | 0.83333 | Palomar is not undergoing maintenance
SDG&E is in blackout (given) | [8 empty] | Successful Blackstart
0
|  | 0.087745 | All 4 critical neighboring interconnect utilities affected
0
[10 empty] | 0.83333 | Pio Pico is available
Successful Blackstart
[6 empty] | 0.16667 | Palomar is unavailable (2 months/year)
[8 empty] | 0 |  | 16.67% | Pio Pico is unavailable
failure to blackstart
Blackout greater than 8 hours: |  |  |  | 0.0057223
79.5% of the time
|  | 0.91225 | At least one neighbor on interconnect is not blacked out | [6 empty] | 0.9375 | Batteries work for either (or both) Palomar cranking paths |  |  |  |  | 0.75 | Batteries work for Pio Pico's 1 cranking path
[5 empty] | Successful Blackstart | [6 empty] | Successful Blackstart | [5 empty] | Successful Blackstart
SDG&E is in blackout (given) | [5 empty] | 83.33% | Palomar is available | [5 empty] | 0.83333 | Pio Pico is available
|  | 0.087745 | All 4 critical neighboring interconnect utilities affected | [6 empty] | 0.0625 | Batteries fail for both Palomar cranking paths |  |  |  |  | 0.25 | Batteries fail for Pio Pico's 1 cranking path
failure to blackstart
[13 empty] | 0.16667 | Pio Pico is unavailable
failure to blackstart
[13 empty] | 0.75 | Batteries work for Pio Pico's 1 cranking path
Successful Blackstart
[10 empty] | 0.83333 | Pio Pico is available
[6 empty] | 16.67% | Palomar is unavailable | [5 empty] | 0.25 | Batteries fail for Pio Pico's 1 cranking path
failure to blackstart
[10 empty] | 0.16667 | Pio Pico is unavailable
failure to blackstart

## P2
P2
New Display
Effectiveness
10%
New P2 Likelihood | 0.016432

## P3
P3
Fuel Cells
Less or greater than 8 hours same
P=PN*[0.205*(PPU)+0.795*(PPU)]
P=PN*[PPU]
P=0.022*1/6
New P3 Likelihood | 0.014624

## P of Neighbors out (hidden)
Option 1: 1/25 years = 0.04 | 0.04 | (1/25 years, from http://www.scientificamerican.com/article/2003-blackout-five-years-later/)
Option 2: | 0.00089419 | US Population | 324308477
|  | # of publicly owned utilities | 2013
|  | Average size of utility | 161107.0427
|  | Average size of utility x4 | 644428.1709
(4 simultaneously blackout)
# of events per year effecting 640,000 or more customers
|  | Year | # of events
|  | 2010 | 1
|  | 2012 | 4
|  | 2013 | 1
|  | 2014 | 3
|  | 2015 | 0
|  | Total | 9
|  | Average | 1.8
http://www.oe.netl.doe.gov/OE417_annual_summary.aspx
|  | Average events/# utlities | 0.00089419 | significant 4-utility wide blackout events per utility per year
Option 3: | 0.018257 | Likelihood of SDG&E and neighbors being out simultaneously = once in 30 to 100 years
Option 4: | 0.087745 | palomar and the cranking paths are out, and the neighbors being out = 0.0183, according to the blackout risk
The probability of the neighbors being out = 0.018/(palomar and cranking paths out)

## P1 FaultTree (hidden)
P1
P = P0 * (PP + PCP) (or P0 * PP * PCP?)
P0 = probability of black out
PP = Probability that Palomar is off-line
PCP = Probability that cranking path is unavailable = ????? | [9 empty] | Value Measure | U-Value
| 0.97798 | At least one neighbor on interconnect is not blacked out
Successful Blackstart
[8 empty] | 1 | At least 1 craking path available
Successful Blackstart
SDG&E is in blackout | [5 empty] | 0.83333 | Palomar is not undergoing maintenance
0.018257
(Given) | [7 empty] | 1.411e-07 | Both cranking paths unavailable
failure to blackstart
| 0.022019 | All 4 critical neighboring interconnect utilities affected
|  |  | 0 |  |  |  |  | 0.01 | New path is unavailable
failure to blackstart
[6 empty] | 0.16667 | Palomar is unavailable (2 months/year)
| Option 1: 1/25 years = 0.04 | 0.04 | (1/25 years, from http://www.scientificamerican.com/article/2003-blackout-five-years-later/)
0.00040201 | Option 2: | 0.00089419 | US Population | 324308477 |  |  |  | 0.99 | New path availability
|  |  | # of publicly owned utilities | 2013 | [5 empty] | Successful blackstart
|  |  | Average size of utility | 161107.0427
Path 1 unavailable 89.92 minutes per year, or 0.00017
|  |  | Average size of utility x4 | 644428.1709 |  |  |  | Path 2 unavailable 462.65 minutes per year, or 0.00083
(4 simultaneously blackout)
New likelihood (given SDG&E is in a blackout)
|  |  | # of events per year effecting 640,000 or more customers | [6 empty] | 0.017513
|  |  | Year | # of events
|  |  | 2010 | 1
|  |  | 2012 | 4
|  |  | 2013 | 1
|  |  | 2014 | 3
|  |  | 2015 | 0
|  |  | Total | 9
|  |  | Average | 1.8
http://www.oe.netl.doe.gov/OE417_annual_summary.aspx
|  |  | Average events/# utlities | 0.00089419 | significant 4-utility wide blackout events per utility per year
| Option 3: | 0.018257 | Likelihood of SDG&E and neighbors being out simultaneously = once in 30 to 100 years
| Option 4: | 0.022019 | palomar and the cranking paths are out, and the neighbors being out = 0.0183, according to the blackout risk
The probability of the neighbors being out = 0.018/(palomar and cranking paths out)

## P2 FaultTree (hidden)
P = P0 * PE
P0 = Probability of black out (assumes this is the probability of a massive west coast blackout involving all four critical neighboring interconnect utilities)
PE = Probability of making an error that fails black start
[5 empty] | Value Measure | U-Value
| 0.9817 | At least one neighbor on interconnect is not blacked out
Successful Blackstart
SDG&E is in blackout |  |  | 80% | No error
0.018257 |  |  |  |  | Successful Blackstart
(Given) | 0.0183 | All 4 critical neighboring interconnect utilities affected
|  |  | 20% | Making an error
Failure to blackstart
New likelihood (given SDG&E is in a blackout)
0.00366

## P3 FaultTree (hidden)
P = P0 * PBR * PBAT * PF * P8
Where:
P0 = Probability of neighbors simultaneously blacked out, necessitating blackstart scenario = 0.018 (assumes this is the probability of a massive west coast blackout involving all four critical neighboring interconnect utilities)
PBR = Probability of breaker not operating is the cause of a fail to restart = 0.5
PBAT = Probability that battery system is the reason for the failure = 0.25 | [12 empty] | Value Measure | U-Value
PF = Percent of locations needing backups fuel cells that will have them installed = 1.0 (Note: The project include all breakers in the cranking path)
P8 = Probability of black out lasting eight hours or more = 79.5%
| 0.97798 | At least one neighbor on interconnect is not blacked out
Successful Blackstart
|  |  |  | 0.5 | Breaker operating
SDG&E is in blackout | [11 empty] | Successful Blackstart
0.018257 | 0.022019 | All 4 critical neighboring interconnect utilities affected |  |  |  |  | 0.75 | Battery system not reason for failure
(Given) | [11 empty] | Successful Blackstart
|  |  | PBR | 0.5 | Breaker not operating |  |  |  |  | 0.205 | Blackout lasting less than 8 hours
Successful Blackstart
[6 empty] | PBAT | 0.25 | Battery system reason for failure
[10 empty] | 0.795 | Blackout lasting longer than 8 hours
[9 empty] | P8 |  |  | Failure to blackstart
[5 empty] | 100% | Percent of locations needing backup fuel cells that will have them installed
New likelihood (given SDG&E is in a blackout)
0.0021881

## Reference
| 1 - Risk Starting Value Lookup Question | AA1 Frequency | AA2 Safety Consequence | AA3 Reliability Consequence | AA4 Compliance Consequence | AA5 Financial Consequence | AA6 Baseline Risk Score | Calculated Baseline | Probability |  |  | Consequence
1 | SCG - Cyber Security | 0.18257 | 4 | 6 | 5 | 5 | 44548.1013 | 44548.1013 | 7 | 31.6228 | 7 | 7 | 10000000
2, 8 | SDGE - Climate Change Adaptation | 0.057735 | 4 | 5 | 4 | 5 | 2655.8112 | 2655.8112 | 6 | 3.1623 | 6 | 6 | 1000000
3 | SCG - Employee, Contractor, Customer and Public Safety | 0.57735 | 6 | 4 | 3 | 4 | 233364.9788 | 233364.9788 | 5 | 0.57735 | 5 | 5 | 100000 |  |  | Before
4 | SCG - Records Management | 0.057735 | 5 | 5 | 5 | 4 | 4734.2722 | 4734.2722 | 4 | 0.18257 | 4 | 4 | 10000 |  |  | Safety | [7 empty] | Compliance
5 | SCG - Workforce Planning | 0.57735 | 4 | 4 | 4 | 4 | 5773.5027 | 5773.5027 | 3 | 0.057735 | 3 | 3 | 1000 | Frequency | 7 | [7 empty] | 7
6 | SCG - Workplace Violence | 0.057735 | 6 | 1 | 2 | 3 | 23106.8279 | 23106.8279 | 2 | 0.018257 | 2 | 2 | 100 |  | 6 | [7 empty] | 6
7 | SDGE - Cyber Security | 0.18257 | 4 | 6 | 5 | 5 | 44548.1013 | 44548.1013 | 1 | 0.0054772 | 1 | 1 | 10 |  | 5 | [7 empty] | 5
9 | SDGE - Employee, Contractor & Public Safety | 0.18257 | 6 | 4 | 4 | 3 | 73796.4859 | 73796.4859 | [6 empty] | 4 | [7 empty] | 4
10 | SDGE - Records Management | 0.057735 | 5 | 5 | 5 | 4 | 4734.2722 | 4734.2722 | Weights | [5 empty] | 3 |  |  |  |  | 1 |  |  | 3 |  |  | 1
11 | SDGE - Workforce Planning | 0.057735 | 4 | 3 | 3 | 2 | 255.1888 | 255.1888 | 40% | Safety |  |  |  |  | 2 | [7 empty] | 2
12 | SDGE - Workplace Violence | 0.057735 | 6 | 1 | 2 | 3 | 23106.8279 | 23106.8279 | 20% | Reliability |  |  |  |  | 1 | [7 empty] | 1
13 | SDGE - Aviation Incident | 0.057735 | 6 | 2 | 2 | 3 | 23107.8672 | 23107.8672 | 20% | Compliance | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
14 | SDGE - Distributed Energy Resources (DERs) Safety and Operational Concerns | 0.18257 | 6 | 3 | 3 | 3 | 73139.2188 | 73139.2188 | 20% | Financial | [5 empty] | Impact | [7 empty] | Impact
15 | SDGE - Electric Infrastructure Integrity | 0.18257 | 4 | 4 | 5 | 4 | 5112.0772 | 5112.0772
16 | SDGE - Fail to Black Start | 0.018257 | 6 | 7 | 5 | 5 | 44548.1013 | 44548.1013 | [7 empty] | Reliability | [7 empty] | Finance
17 | SDGE - Major Disturbance to Electrical Service (e.g. Blackout) | 0.018257 | 6 | 7 | 5 | 5 | 44548.1013 | 44548.1013 | [5 empty] | Frequency | 7 | [7 empty] | 7
18 | SDGE - Public Safety Events - Electric | 0.057735 | 5 | 3 | 3 | 3 | 2344.0421 | 2344.0421 | [6 empty] | 6 | [7 empty] | 6
19 | SDGE - Unmanned Aircraft System (UAS) Incident | 0.018257 | 6 | 4 | 3 | 4 | 7379.6486 | 7379.6486 | [6 empty] | 5 | [7 empty] | 5
20 | SDGE - Wildfires caused by SDG&E Equipment (including 3rd Party Pole Attachments) | 0.57735 | 7 | 6 | 5 | 6 | 2551888.1898 | 2551888.1898 | [6 empty] | 4 | [7 empty] | 4
21 | SCG - Catastrophic Damage involving Gas Infrastructure (Dig-Ins) | 0.57735 | 6 | 4 | 3 | 4 | 233364.9788 | 233364.9788 | [6 empty] | 3 |  |  | 1 |  |  |  |  | 3 |  |  | 1
22 | SCG - Catastrophic Damage Involving Gas Transmission Pipeline Failure | 0.057735 | 6 | 5 | 5 | 6 | 36950.4172 | 36950.4172 | [6 empty] | 2 | [7 empty] | 2
23 | SCG - Catastrophic Damage involving Medium and Non-DOT Pipeline Failure | 0.057735 | 5 | 3 | 3 | 3 | 2344.0421 | 2344.0421 | [6 empty] | 1 | [7 empty] | 1
24 | SCG - Catastrophic Event related to Storage Well Integrity | 0.018257 | 5 | 5 | 5 | 5 | 1825.7419 | 1825.7419 | [7 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
25 | SCG - Physical Security of Critical Infrastructure | 0.057735 | 5 | 6 | 4 | 4 | 14087.3466 | 14087.3466 | [7 empty] | Impact | [7 empty] | Impact
26 | SDGE - Catastrophic Damage involving Gas Infrastructure (Dig-Ins) | 0.57735 | 6 | 4 | 3 | 4 | 233364.9788 | 233364.9788
27 | SDGE - Catastrophic Damage Involving Gas Transmission Pipeline Failure | 0.018257 | 6 | 4 | 5 | 6 | 11356.1144 | 11356.1144 | [7 empty] | After
28 | SDGE - Catastrophic Damage Involving Medium and non-DOT Pipeline Failure | 0.057735 | 5 | 3 | 3 | 3 | 2344.0421 | 2344.0421 | [7 empty] | Safety | [7 empty] | Compliance
| SDGE - Violation of Environmental Policies/Procedures | 0.057735 | 4 | 1 | 5 | 4 | 1501.2262 | 1501.2262 | [5 empty] | Frequency | 7 | [7 empty] | 7
[15 empty] | 6 | [7 empty] | 6
[15 empty] | 5 | [7 empty] | 5
[15 empty] | 4 | [7 empty] | 4
[15 empty] | 3 |  |  |  |  | 1 |  |  | 3 |  |  | 1
[15 empty] | 2 | [7 empty] | 2
[15 empty] | 1 | [7 empty] | 1
[16 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
[16 empty] | Impact | [7 empty] | Impact
[16 empty] | Reliability | [7 empty] | Finance
[14 empty] | Frequency | 7 | [7 empty] | 7
[15 empty] | 6 | [7 empty] | 6
[15 empty] | 5 | [7 empty] | 5
[15 empty] | 4 | [7 empty] | 4
[15 empty] | 3 |  |  | 1 |  |  |  |  | 3 |  |  | 1
[15 empty] | 2 | [7 empty] | 2
[15 empty] | 1 | [7 empty] | 1
[16 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
[16 empty] | Impact | [7 empty] | Impact